Dataset Metadata

Jordan National Water Distribution Network — Spatial A-B Sensor Dataset  v2.0

AI-Driven Zonal Water Loss Detection and Smart Resource Management

Change The Future Team  ·  Amman Arab University  ·  Supervised by Dr. Mais Ahmad Haj Qasem  ·  IEEE RAS & CS Hackathon 2026

# 1. Dataset Overview

This dataset is a physics-calibrated synthetic dataset designed to support an AI-driven spatial water loss detection system for the Jordanian national water distribution network. It implements a spatial A-B sensor pair architecture, where each record represents a physical pipe segment between two measurement points (Sensor A → Sensor B), rather than a single-point time-series.

The dataset is calibrated to real Jordanian operational parameters sourced from the Ministry of Water and Irrigation (MWI Facts & Figures 2022), FAO AQUASTAT, and the World Bank Jordan Water Sector Public Expenditure Review (2022). Key national statistics reflected include a Non-Revenue Water (NRW) rate of 41–56%, per-capita water availability of ~145 m³/year, and intermittent supply schedules of 6–14 hours per day depending on governorate.

| Property | Training set | Test set | Total |
| --- | --- | --- | --- |
| Total rows | 80,000 | 20,000 | 100,000 |
| Anomaly rate | 20.0% | 5.0% | — |
| Columns | 39 | 39 | 39 |
| Governorates | 12 | 12 | 12 |
| Zones (DMAs) | 31 | 31 | 31 |
| Missing values | 0 | 0 | 0 |
| Date range | 2020-01-01 | 2023-06-01 | — |

# 2. Data Split Strategy & Validation Philosophy

The dataset is divided into two files only: training (80%) and test (20%). No separate validation file is provided. This is a deliberate design decision:

(1) Validation is extracted dynamically inside the training pipeline using StratifiedShuffleSplit(test_size=0.15) applied to the shuffled training set, after shuffling but before scaling. This prevents temporal data leakage between splits.

(2) The test set reflects realistic operational conditions with only 5% anomaly rate — matching real-world NRW patterns in Jordanian DMAs.

(3) The training set uses 20% anomaly rate to ensure sufficient examples of each fault class during supervised learning.

Scalers (StandardScaler) are fitted exclusively on the training split and applied to validation and test to prevent data leakage.

# 3. Class Distribution and Balance Rationale

The four classes reflect the primary fault categories defined by the IWA Water Loss Task Force and adapted to Jordanian DMA conditions. The class ratios are intentionally designed to reflect both training needs (balanced enough to learn minority classes) and realistic operational conditions (test set is heavily skewed toward normal).

| Class | Train n | Train % | Test n | Test % | Severity mean | Severity range | ΔFlow% mean | DP_Dev mean |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Normal | 64,000 | 80.00% | 19,000 | 95.00% | 0.00 | 0.00 | 1.785 | 0.042 |
| Leak | 7,200 | 9.00% | 450 | 2.25% | 0.106 | 0.03–0.18 | 10.779 | 2.835 |
| Burst | 4,000 | 5.00% | 250 | 1.25% | 0.487 | 0.25–0.72 | 48.625 | 19.130 |
| Theft | 4,800 | 6.00% | 300 | 1.50% | 0.096 | 0.05–0.14 | 9.667 | 0.464 |

Anomaly distribution within anomalous samples (training): Leak 45%, Theft 30%, Burst 25%. This reflects the relative frequency of these fault types in aging Jordanian pipe infrastructure according to MWI operational reports.

# 4. Governorate Configuration

All 12 Jordan governorates are included. Each governorate is configured with independently calibrated hydraulic and demographic parameters. These parameters determine the demand multiplier, baseline flow ranges, and anomaly probability for every zone.

| Governorate | Train rows | Test rows | Arabic | Environment | Pipe material | Age (yr) | NRW | Supply | Zones |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Amman | 13,017 | 3,231 | عمّان | urban | ductile iron | 18 | 43% | 12 hrs | 5 |
| Irbid | 10,090 | 2,623 | إربد | urban | ductile iron | 24 | 45% | 10 hrs | 4 |
| Zarqa | 7,727 | 1,917 | الزرقاء | urban-industrial | cast iron | 35 | 52% | 8 hrs | 3 |
| Balqa | 7,677 | 1,947 | البلقاء | mixed | PVC | 16 | 47% | 9 hrs | 2 |
| Mafraq | 7,731 | 1,903 | المفرق | desert | HDPE | 13 | 50% | 7 hrs | 3 |
| Karak | 5,294 | 1,332 | الكرك | rural | asbestos cement | 48 | 56% | 6 hrs | 2 |
| Maan | 5,220 | 1,292 | معان | desert | HDPE | 15 | 55% | 6 hrs | 2 |
| Aqaba | 5,216 | 1,281 | العقبة | coastal-desert | ductile iron | 22 | 41% | 14 hrs | 2 |
| Madaba | 5,148 | 1,252 | مادبا | rural | PVC | 22 | 51% | 8 hrs | 2 |
| Jerash | 5,129 | 1,289 | جرش | mixed | PVC | 19 | 48% | 8 hrs | 2 |
| Ajloun | 5,100 | 1,272 | عجلون | rural | asbestos cement | 40 | 54% | 7 hrs | 2 |
| Tafilah | 2,651 | 661 | الطفيلة | rural | PVC | 25 | 53% | 6 hrs | 1 |

# 5. Key Numeric Statistics (Training Set — 80,000 rows)

| Feature | Min | Max | Mean | Std dev |
| --- | --- | --- | --- | --- |
| Flow_A (L/min) | 0.38 | 120.0 | 23.79 | 20.33 |
| Pressure_A (PSI) | 14.9 | 85.0 | 48.42 | 15.07 |
| Flow_B (L/min) | 0.01 | 119.9 | 22.56 | 19.63 |
| Pressure_B (PSI) | 2.65 | 85.0 | 45.92 | 15.18 |
| Distance_AB (m) | 52.8 | 543.4 | 289.97 | 149.32 |
| Delta_Flow (L/min) | 0.00 | 81.68 | 1.23 | 3.69 |
| Delta_Pressure (PSI) | 0.00 | 77.06 | 2.50 | 5.13 |
| Delta_Flow_Pct (%) | 0.00 | 99.81 | 5.41 | 11.51 |
| DP_Predicted (PSI) | 0.02 | 28.54 | 1.23 | 2.20 |
| DP_Deviation (PSI) | -1.29 | 52.02 | 1.27 | 4.60 |
| Flow_DP_Ratio (L/PSI) | 0.00 | 11.68 | 0.42 | 0.52 |
| Severity (fraction) | 0.00 | 0.72 | 0.040 | 0.114 |

# 6. Column Reference — All 39 Columns

## 6.1 Identifier Columns (not used as model inputs)

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Timestamp | String (ISO) | — | 2020-01-01 00:00 – 2023-12-31 23:45 | Observation timestamp at 15-minute intervals. Used for time alignment. |
| Governorate | String | — | 12 distinct values | One of 12 Jordan governorates. Encodes regional hydraulic and demographic context. |
| Zone_ID | String | — | 31 distinct zones | Distribution Management Area (DMA) identifier within the governorate. |
| Segment_ID | String | — | Composite key | Gov-Zone-Distance composite. Uniquely identifies each A-B pipe segment. |

## 6.2 Time / Contextual Columns

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| hour | Integer | — | 0 – 23 | Hour of day. Drives the diurnal demand pattern (peaks 07:00–09:00 and 18:00–21:00). |
| day_of_week | Integer | — | 0 (Mon) – 6 (Sun) | Day index. Jordan weekend = Thursday (3) and Friday (4). |
| month | Integer | — | 1 – 12 | Calendar month used to encode seasonal demand multiplier. |
| is_ramadan | Binary {0,1} | — | 1 = Ramadan month | 1 during Ramadan fasting month. Demand shifts from daytime to Iftar/Suhoor windows. |
| is_eid | Binary {0,1} | — | 1 = Eid day | 1 on Eid Al-Fitr / Eid Al-Adha. Demand spike of +30–55% above baseline. |
| is_summer | Binary {0,1} | — | 1 = June–August | Summer indicator. Demand rises 25–55% depending on governorate. |
| is_winter | Binary {0,1} | — | 1 = Dec–February | Winter indicator. Demand drops 10–22%. |
| is_weekend | Binary {0,1} | — | 1 = Thu or Fri | Jordan-specific weekend flag. Adds ~12% to daily demand. |
| supply_on | Binary {0,1} | — | 0 or 1 | 1 when supply schedule is active. Jordan: intermittent 6–14 hours/day by governorate. |

## 6.3 Governorate Profile Columns

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| population_density | Float | persons/km² | 4 – 732 | Persons per km² for the governorate. Proxy for baseline demand intensity. |
| environment_code | Integer | — | 0–5 | 0=urban, 1=urban-industrial, 2=mixed, 3=rural, 4=desert, 5=coastal-desert. |
| pipe_age_years | Integer | years | 13 – 48 | Average pipe age. Older pipes have higher roughness, lower C-coefficient, higher NRW. |
| hw_coefficient | Float | dimensionless | 65 – 150 | Hazen-Williams C coefficient. Decreases with age and material degradation. |
| elevation_m | Integer | metres | 5 – 1200 | Mean zone elevation above sea level. Affects static pressure and pumping energy. |
| nrw_rate | Float | fraction | 0.41 – 0.56 | Non-Revenue Water rate per governorate. Used to calibrate background leakage. |

## 6.4 Sensor A — Upstream Readings

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Flow_A | Float | L/min | 0.38 – 120.0 | Volumetric flow rate at upstream sensor A. Represents network input to the segment. |
| Pressure_A | Float | PSI | 14.9 – 85.0 | Hydraulic pressure at node A. Governed by governorate pump head settings. |

## 6.5 Sensor B — Downstream Readings

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Flow_B | Float | L/min | 0.01 – 119.9 | Volumetric flow rate at downstream sensor B. Always ≤ Flow_A (mass balance). |
| Pressure_B | Float | PSI | 0.5 – 85.0 | Hydraulic pressure at node B. Lower than Pressure_A due to friction + anomalous losses. |

## 6.6 Environmental Reading

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Temp_Water | Float | °C | 6.0 – 32.0 | Water temperature. Affects viscosity and friction coefficient. |

## 6.7 Spatial Configuration

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Distance_AB | Float | metres | 52.8 – 543.4 | Physical pipe distance between sensor A and sensor B. |

## 6.8 Derived Spatial Features (core ML signals)

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Delta_Flow | Float | L/min | 0 – 81.7 | Flow_A − Flow_B. Core leakage signal. Positive = water lost between A and B. |
| Delta_Pressure | Float | PSI | 0 – 77.1 | Pressure_A − Pressure_B. Combines friction loss + any anomalous pressure deviation. |
| Delta_Flow_Pct | Float | % | 0 – 99.8 | Delta_Flow / Flow_A × 100. Normalised loss fraction. Normal < 3%; Burst > 20%. |
| Delta_Pressure_Pct | Float | % | 0 – 99.8 | Delta_Pressure / Pressure_A × 100. Normalised pressure change. |
| Flow_Ratio | Float [0–1] | dimensionless | 0 – 1.0 | Flow_B / Flow_A. Delivery efficiency. Normal ≈ 0.97–0.99. |
| Pressure_Ratio | Float [0–1] | dimensionless | 0 – 1.0 | Pressure_B / Pressure_A. Near 1 for theft; significantly < 1 for leak/burst. |
| Loss_Per_100m | Float | L/min/100m | 0 – 99+ | Delta_Flow / (Distance_AB/100). Normalises loss by segment length. |
| DP_Predicted | Float | PSI | 0.02 – 28.5 | Physics-predicted pressure drop: Darcy-Weisbach + Churchill friction factor (1977). |
| DP_Deviation | Float | PSI | -1.3 – 52.0 | Delta_Pressure − DP_Predicted. Excess loss above friction model. Key anomaly signal. |
| Flow_DP_Ratio | Float | L/min/PSI | 0 – 11.7 | Delta_Flow / max(¦Delta_Pressure¦, 0.10). Primary theft discriminator; high = large flow loss with minimal pressure impact. |

## 6.9 Target / Label Columns (NEVER use as model inputs)

| Column | Data type | Unit | Range / Values | Description |
| --- | --- | --- | --- | --- |
| Anomaly_Type | String | — | normal/leak/burst/theft | Ground-truth fault class. PRIMARY TARGET — never use as model input. |
| Anomaly_Label | Integer [0–3] | — | 0=normal,1=leak,2=burst,3=theft | Encoded Anomaly_Type for classifier. TARGET ONLY. |
| Anomaly_Binary | Binary {0,1} | — | 0=normal, 1=anomaly | 1 if any anomaly. Used for AUC-ROC and Isolation Forest evaluation. TARGET ONLY. |
| Severity | Float [0–0.72] | fraction | 0 for normal; >0 for faults | Fraction of Flow_A lost due to anomaly. 0 for normal. Regression target if needed. TARGET ONLY. |

# 7. Hydraulic Physics Engine

## 7.1 Pressure Drop Model

Pressure drop between sensors A and B is modelled using the Darcy-Weisbach equation with the Churchill (1977) approximation for the Darcy friction factor, valid for all Reynolds number regimes (laminar, transitional, and fully turbulent). An 8% minor loss factor (bends, fittings, joints) is added to the friction term.

Pipe roughness values (ε, mm): ductile iron = 0.26, cast iron = 0.26, PVC = 0.0015, HDPE = 0.007, asbestos cement = 0.30.

Pipe diameters: 50 mm for urban/industrial governorates (Amman, Zarqa, Irbid, Balqa, Mafraq, Aqaba, Madaba); 40 mm for rural/smaller governorates (Karak, Jerash, Ajloun, Tafilah, Maan).

## 7.2 Anomaly Injection Models

Each anomaly type has a distinct hydraulic signature:

Normal — Background seepage: loss rate = 0.004 × (dist/100m) × age_factor × (NRW/0.40). Physically consistent with IWA Unavoidable Annual Real Losses.

Leak — Severity ~ Uniform(0.03, 0.18). Extra pressure drop = sev × P_A × Uniform(0.35, 0.75). Orifice model for crack or joint failure.

Burst — Severity ~ Uniform(0.25, 0.72). Extra pressure drop = sev × P_A × Uniform(0.70, 0.92). Catastrophic pipe rupture.

Theft — Severity ~ Uniform(0.05, 0.14). Extra pressure drop = sev × P_A × Uniform(0.04, 0.16). Small illegal tap: minimal pressure impact, elevated Flow_DP_Ratio.

## 7.3 Jordan Demand Model

Water demand is scaled by a multiplier that captures: seasonal variation (summer peak +25–55%, winter −10–22%), Islamic calendar events (Ramadan daytime −35–45%, Iftar/Suhoor spike +45–62%, Eid +30–55%), Jordan-specific weekend effect (Thursday–Friday +12%), and a standard diurnal curve with peaks at 07:00–09:00 and 18:00–21:00.

# 8. How the Dataset Supports Each ML Model Stage

## Stage 1 — LSTM Demand Predictor

Trained on NORMAL samples only. Learns expected Delta_Flow and Delta_Pressure for normal hydraulic conditions. Outputs: LSTM residuals (actual − predicted) fed as features to downstream models. Key LSTM inputs: Flow_A, Pressure_A, Distance_AB, all time and profile features (19 total).

## Stage 2 — Isolation Forest Anomaly Detection

Unsupervised. Trained on spatial delta features of NORMAL samples only. Learns the normal A-B relationship without using labels. Contamination = 0.05 (matching realistic 5% test anomaly rate). Key IF inputs: all 11 Derived spatial features.

## Stage 3 — Random Forest Fault Classifier

Supervised. Input = all spatial + profile features + IF score + IF confidence + IF flag + LSTM residuals (33 features total). class_weight='balanced' to handle imbalance. Classifies: normal / leak / burst / theft.

## Stage 4 — Decision Engine

Ensemble confidence = 0.30 × IF_confidence + 0.70 × RF_proba(anomaly). Alert fires if (IF_flag=1 OR RF_pred>0) AND ensemble_confidence ≥ 0.45. Burst recall = 1.000 is the primary safety metric.

# 9. Data Leakage Prevention

The following columns are TARGET columns only — they must NEVER be used as model inputs:

•  Anomaly_Type  —  string class label

•  Anomaly_Label  —  encoded integer class

•  Anomaly_Binary  —  binary fault indicator

•  Severity  —  fault severity fraction

The training data is shuffled before the internal validation split to remove temporal ordering bias introduced by the sequential timestamp generation pattern.

Scalers are fitted exclusively on the training partition (after validation is separated). Validation and test partitions are transformed only — never used for fitting.

# 10. Assumptions and Limitations

(1) All data is synthetically generated. No real sensor readings from WAJ, Miyahuna, or other Jordanian water utilities were used. Validation against real operational data is identified as future work.

(2) Pipe diameter is fixed at 50 mm or 40 mm per zone type. Real DMA networks exhibit heterogeneous diameters within the same zone.

(3) Demand multipliers are approximated from monthly averages. Sub-monthly demand events (school terms, industrial shifts, tourist seasons) are not modelled.

(4) Sensor noise is modelled as Gaussian. Real IoT sensors may exhibit non-Gaussian drift, outliers, and communication failures.

(5) The dataset does not model water hammer, transient pressure events, or temperature-dependent viscosity changes.

(6) Physics was calibrated against LeakDB and BattLeDIM benchmark parameters but not directly validated against those datasets due to schema incompatibility (those datasets use node-based single-point sensing, not A-B spatial pairs).

# 11. Citation and Reference Datasets

This dataset should be cited as:

Change The Future Team, Amman Arab University. (2026). Jordan National Water Distribution Network — Spatial A-B Sensor Synthetic Dataset v2.0. AI-Driven Zonal Water Loss Detection Project. IEEE RAS & CS Hackathon.

Physics calibration references:

Vrachimis et al. (2018). LeakDB: A Benchmark Dataset for Leakage Diagnosis in Water Distribution Networks. WDSA/CCWI Joint Conference. https://github.com/KIOS-Research/LeakDB

Vrachimis et al. (2020). BattLeDIM: Battle of the Leakage Detection and Isolation Methods. Zenodo. https://doi.org/10.5281/zenodo.4017659

Churchill, S. W. (1977). Friction factor equation spans all fluid-flow regimes. Chemical Engineering, 84(24), 91–92.

Jordan Ministry of Water and Irrigation. (2022). Jordan Water Sector Facts and Figures 2022.

World Bank. (2022). Jordan Public Expenditure Review: Water Sector.